## CM_ HeatLoad
Tom Peterson
Revised for TDP parameters 26 June 2012
Iteration of this heat load table with input from Chris Adolphsen, 5 Jan 07 | [12 empty] | 10 Hz LP KCS e- (e- source baseline)
| TESLA numbers provide basis for scaling, RDR numbers for reference | [9 empty] | positron beam |  | positron production |  | electron beam
Cryomodule | TESLA |  | ILC 9-8-9 (RDR) |  | RDR revised* |  | TDR M Linac KCS |  | TDR M Linac DKS |  | 5 Hz LP KCS e+ |  | 1/2 of 10 Hz LP KCS e- |  | 1/2 of 10 Hz LP KCS e- |  | ILC 9-8-9 refers to the number of cavities in the modules in a ML unit
E, [MV/m] | 23.4 |  | 31.5 |  | 31.5 |  | 31.5 |  | 31.5 |  | 24.1 |  | 23.7 |  | 23.7 |  | G
Q | 10000000000 |  | 10000000000 |  | 10000000000 |  | 10000000000 |  | 10000000000 |  | 10000000000 |  | 10000000000 |  | 10000000000
Rep rate, [Hz] | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5
Number of Cavities | 12 |  | 8.6667 |  | 8.6667 |  | 8.6667 |  | 8.6667 |  | 8 |  | 8 |  | 8 |  | avg number of cavities per module
Fill time [µsec] | 420 |  | 597.1478 |  | 597.1478 |  | 924 |  | 924 |  | 471 |  | 463 |  | 463 |  | Tf |  |  | 2008-03-01 | after RDR
Beam pulse [µsec] | 950 |  | 969 |  | 969 |  | 727 |  | 727 |  | 727 |  | 727 |  | 727 |  | Tb |  |  | Substitute the data below
Number of bunches | 2820 |  | 2670 |  | 2670 |  | 1312 |  | 1312 |  | 1312 |  | 1312 |  | 1312 |  | Nb |  |  | for the TESLA TDR numbers
Particles per bunch [1e10] | 2 |  | 2.04 |  | 2.04 |  | 1.9974 |  | 1.9974 |  | 2.9962 |  | 2.9962 |  | 2.9962 |  | Qb |  |  | Coupler data from Linac 2004
Beam current (mA) | 9.5108 |  | 9.0049 |  | 9.0049 |  | 5.8 |  | 5.8 |  | 8.7 |  | 8.7 |  | 8.7 |  |  |  |  | by W-D Moeller et. al.
Gfac |  |  | 2.088 |  | 2.088 |  | 2.2426 |  | 2.2426 |  | 0.9361 |  | 0.89885 |  | 0.89885 |  | Stored Energy Factor = G^2*(Tb + 1.1*Tf) |  |  | 2 K | 4 K | 70 K
Pfac |  |  | 1.5404 |  | 1.5404 |  | 1.1758 |  | 1.1758 |  | 0.87461 |  | 0.85184 |  | 0.85184 |  | Input Power Factor = G*(Tb + 2*Tf)*Cfac |  | 0 power | 0.02 | 0.2 | 1.9
Bfac |  |  | 0.98506 |  | 0.98506 |  | 0.46406 |  | 0.46406 |  | 1.0441 |  | 1.0441 |  | 1.0441 |  | Bunch Factor = Nb*Qb^2 |  | TESLA | 0.06 | 0.5 | 6
Cfac |  |  | 0.94681 |  | 0.94681 |  | 0.60718 |  | 0.60718 |  | 0.91077 |  | 0.91077 |  | 0.91077 |  | Beam Current Factor = Qb*Nb/Tb |  | my conclusion net dyn | 0.04 | 0.3 | 4.1
| Static | Dynamic | Static | Dynamic | Static | Dynamic | Static | Dynamic | Static | Dynamic | Static | Dynamic | Static | Dynamic | Static | Dynamic
Temperature Level | 2K |  | 2K |  | 2K |  | 2K |  | 2K |  | 2K |  | 2K |  | 2K
RF load |  | 4.95 |  | 7.4648 |  | 7.4648 |  | 8.0174 |  | 8.0174 |  | 3.0891 |  | 2.9662 |  | 2.9662 | Dynamic load scaled by the number of cavities and Gfac
Supports | 0.6 |  | 0.6 | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0 | Assume independent of number of cavities
Input coupler | 0.24 | 0.48 | 0.55 | 0.16 | 0.17333 | 0.53399 | 0.17333 | 0.40761 | 0.17333 | 0.40761 | 0.16 | 0.27987 | 0.16 | 0.27259 | 0.16 | 0.27259 | Static load scaled by number of cavities, dynamic by Pfac also
HOM coupler (cables) | 0.01 | 0.27 | 0.0072222 | 0.18463 | 0.0072222 | 0.18463 | 0.0072222 | 0.1184 | 0.0072222 | 0.1184 | 0.0066667 | 0.16394 | 0.0066667 | 0.16394 | 0.0066667 | 0.16394 | Static and dynamic load scaled by number of cavities, dynamic by Cfac also
HOM absorber | 0.14 | 0.02 | 0.14 | 0.019701 | 0.14 | 0.019701 | 0.14 | 0.006703 | 0.14 | 0.006703 | 0.14 | 0.013922 | 0.14 | 0.013922 | 0.14 | 0.013922 | Dynamic load scaled by Bfac
Beam tube bellows |  | 0.24 |  | 0.36193 |  | 0.36193 |  | 0.38872 |  | 0.38872 |  | 0.14978 |  | 0.14382 |  | 0.14382 | Dynamic load scaled by the number of cavities and Gfac
Current leads | 0.036667 |  | 0.28333 | 0.28333 | 0.28333 | 0.28333 | 0.28333 | 0.28333 | 0.28333 | 0.28333 | 1.7 | 1.7 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | For ML weigh by a factor of 1/3 since only 1 in 3 modules have quads**
HOM to structure |  | 1.68 |  | 1.1952 |  | 1.1952 |  | 0.56305 |  | 0.56305 |  | 1.1694 |  | 1.1694 |  | 1.1694 | Static load scaled by the number of cavities, dynamic by Bfac also
Coax cable (4) | 0.05 |  | 0.05 |  | 0.05 |  | 0.05 |  | 0.05 |  | 0.05 |  | 0.05 |  | 0.05 |  | Assume indepent of number of cavities
Instrumentation taps | 0.07 |  | 0.07 |  | 0.07 |  | 0.07 |  | 0.07 |  | 0.07 |  | 0.07 |  | 0.07 |  | Assume indepent of number of cavities
Scales as Gfac |  | 5.19 |  | 7.8267 |  | 7.8267 |  | 8.4061 |  | 8.4061 |  | 3.2389 |  | 3.11 |  | 3.11
Scales as Pfac |  | 0.48 |  | 0.16 |  | 0.53399 |  | 0.40761 |  | 0.40761 |  | 0.27987 |  | 0.27259 |  | 0.27259
Independent of G,Tf | 1.1467 | 1.97 | 1.7006 | 1.6829 | 1.3239 | 1.6829 | 1.3239 | 0.97149 | 1.3239 | 0.97149 | 2.7267 | 3.0473 | 1.5962 | 1.9168 | 1.5962 | 1.9168
Static, dynamic sum | 1.1467 | 7.64 | 1.7006 | 9.6696 | 1.3239 | 10.0436 | 1.3239 | 9.7852 | 1.3239 | 9.7852 | 2.7267 | 6.5661 | 1.5962 | 5.2994 | 1.5962 | 5.2994 | Total for 9-8-9 TDR KCS RF unit below | Total for one cavity below
2K Sum [W] | 8.7867 |  | 11.3701 |  | 11.3675 |  | 11.1091 |  | 11.1091 |  | 9.2927 |  | 6.8956 |  | 6.8956 |  | 33.3273 | 0.99005 | 1.2818
| 5K |  | 5K |  | 5K |  | 5K |  | 5K |  | 5K |  | 5K |  | 5K
Radiation | 1.95 |  | 1.4083 |  | 1.4083 |  | 1.4083 |  | 1.4083 |  | 1.3 |  | 1.3 |  | 1.3 |  | Static load scaled by number of cavities
Supports | 2.4 |  | 2.4 |  | 2.4 |  | 2.4 |  | 2.4 |  | 2.4 |  | 2.4 |  | 2.4 |  | Assume indepent of number of cavities
Input coupler | 2.4 | 3.6 | 1.48 | 1.32 | 1.7333 | 4.0049 | 1.7333 | 3.0571 | 1.7333 | 3.0571 | 1.6 | 2.0991 | 1.6 | 2.0444 | 1.6 | 2.0444 | Static load scaled by number of cavities, dynamic by Pfac also
HOM coupler (cables) | 0.4 | 2.66 | 0.28889 | 1.8189 | 0.28889 | 1.8189 | 0.28889 | 1.1665 | 0.28889 | 1.1665 | 0.26667 | 1.6151 | 0.26667 | 1.6151 | 0.26667 | 1.6151 | Static and dynamic load scaled by number of cavities, dynamic by Cfac also
HOM absorber | 3.13 | 0.77 | 3.13 | 0.7585 | 3.13 | 0.7585 | 3.13 | 0.35732 | 3.13 | 0.35732 | 3.13 | 0.80398 | 3.13 | 0.80398 | 3.13 | 0.80398 | Dynamic load scaled by Bfac
Current leads |  |  | 0.46667 | 0.46667 | 0.46667 | 0.46667 | 0.46667 | 0.46667 | 0.46667 | 0.46667 | 2.8 | 2.8 | 0.938 | 0.938 | 0.938 | 0.938 | For ML weigh by a factor of 1/3 since only 1 in 3 modules have quads**
Diagnostic cable | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | 1.39 | 0 | Assume independent of number of cavities
Scales as Pfac |  | 3.6 |  | 1.32 |  | 4.0049 |  | 3.0571 |  | 3.0571 |  | 2.0991 |  | 2.0444 |  | 2.0444
Independent of G,Tf | 11.67 | 3.43 | 10.5639 | 3.0441 | 10.8172 | 3.0441 | 10.8172 | 1.9904 | 10.8172 | 1.9904 | 12.8867 | 5.2191 | 11.0247 | 3.3571 | 11.0247 | 3.3571
Static, dynamic sum | 11.67 | 7.03 | 10.5639 | 4.3641 | 10.8172 | 7.049 | 10.8172 | 5.0475 | 10.8172 | 5.0475 | 12.8867 | 7.3181 | 11.0247 | 5.4015 | 11.0247 | 5.4015 | Total for 9-8-9 TDR KCS RF unit below
5K Sum [W] | 18.7 |  | 14.928 |  | 17.8662 |  | 15.8648 |  | 15.8648 |  | 20.2048 |  | 16.4262 |  | 16.4262 |  | 47.5943
| 40K |  | 40K |  | 40K |  | 40K |  | 40K |  | 40K |  | 40K |  | 40K
Radiation | 44.99 |  | 32.4928 |  | 32.4928 |  | 32.4928 |  | 32.4928 |  | 29.9933 |  | 29.9933 |  | 29.9933 |  | Static load scaled by number of cavities
Supports | 6 |  | 6 |  | 18 |  | 18 |  | 18 |  | 18 |  | 18 |  | 18 |  | Assume indepent of number of cavities | Note: Paolo says post heat at 40 K in TDR was low by factor 3, so 3 X TESLA
Input coupler | 22.8 | 49.2 | 15.51 | 66.08 | 16.4667 | 54.7338 | 16.4667 | 41.7803 | 16.4667 | 41.7803 | 15.2 | 28.6871 | 15.2 | 27.9405 | 15.2 | 27.9405 | Static load scaled by number of cavities, dynamic by Pfac also |  |  | above post heat updated after RDR
HOM coupler (cables) | 2.55 | 13.22 | 1.8417 | 9.0399 | 1.8417 | 9.0399 | 1.8417 | 5.7972 | 1.8417 | 5.7972 | 1.7 | 8.0269 | 1.7 | 8.0269 | 1.7 | 8.0269 | Static and dynamic load scaled by number of cavities, dynamic by Cfac also
HOM absorber | -3.27 | 15.27 | -3.27 | 15.0419 | -3.27 | 15.0419 | -3.27 | 7.0861 | -3.27 | 7.0861 | -3.27 | 15.9438 | -3.27 | 15.9438 | -3.27 | 15.9438 | Dynamic load scaled by Bfac
Current leads | 13 | 5 | 4.1333 | 4.1333 | 4.1333 | 4.1333 | 4.1333 | 4.1333 | 4.1333 | 4.1333 | 24.8 | 24.8 | 8.308 | 8.308 | 8.308 | 8.308 | For ML weigh by a factor of 1/3 since only 1 in 3 modules have quads**
Diagnostic cable | 5.38 |  | 2.48 |  | 5.38 |  | 5.38 |  | 5.38 |  | 5.38 |  | 5.38 |  | 5.38 |  | Assume indepent of number of cavities
Scales as Pfac |  | 49.2 |  | 66.08 |  | 54.7338 |  | 41.7803 |  | 41.7803 |  | 28.6871 |  | 27.9405 |  | 27.9405
Independent of G,Tf | 91.45 | 33.49 | 59.1878 | 28.2151 | 75.0444 | 28.2151 | 75.0444 | 17.0167 | 75.0444 | 17.0167 | 91.8033 | 48.7707 | 75.3113 | 32.2787 | 75.3113 | 32.2787
Static, dynamic sum | 91.45 | 82.69 | 59.1878 | 94.2951 | 75.0444 | 82.9489 | 75.0444 | 58.7969 | 75.0444 | 58.7969 | 91.8033 | 77.4577 | 75.3113 | 60.2192 | 75.3113 | 60.2192 | Total for 9-8-9 TDR KCS RF unit below
40K Sum [W] | 174.14 |  | 153.4829 |  | 157.9934 |  | 133.8414 |  | 133.8414 |  | 169.2611 |  | 135.5305 |  | 135.5305 |  | 401.5242
* | RDR revised includes two updates following the RDR. One is a correction for the supports heat load at 40 K. The other an updated set of input coupler heat loads at all temperature levels.
** | Current lead heat scaled from LHC Project Report 691 for 3 100 A pair (quad + two correctors), full current heat = 2 x no current.
** | e+ booster has on average 2 quads per cryomodule, so factor 2 for lead heat, based on " ILC cryo RF layout labels.xlsx "
** | e- booster has on average 2/3 quad per cryomodule, so factor 0.67 for lead heat based on " ILC cryo RF layout labels.xlsx "

## RDR
Tom Peterson |  |  | ILC Cryogenic Power Estimates
2006-12-29
This version: | ILC at 31.5 MV/m, 1.0x10^10, 5 Hz
1 standard cryogenic unit of 250 GeV linac.
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
2.4723
Total heat load (dynamic plus static) for 9-8-9 RF units, full cryogenic unit
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-8-8-8-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 192 | modules in this cryogenic unit (longest anticipated)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 59.1878 | 10.5639 | 1.7006 |  | Heat loads per CM_HeatLoad sheet
Predicted module dynamic heat load | (W/module) | 94.2951 | 4.3641 | 9.6696
Number of modules per cryo unit (9-8-9-cavity modules) |  | 192 | 192 | 192
Total module static heat per cryo unit | (kW) | 11.3641 | 2.0283 | 0.32651
Total module dynamic heat per cryo unit | (kW) | 18.1047 | 0.8379 | 1.8566
Non-module heat load per cryo unit | (kW) | 1 | 0.2 | 0.2 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 30.4687 | 3.0662 | 2.3831 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 146.0069 | 95.6684 | 115.3635 |  |  | times 20 boxes per cryo unit
Ideal power based on total estimated heat | (kW) | 140.308 | 145.6599 | 368.5569
Heat uncertainty factor on static heat (Fus) |  | 1.1 | 1.1 | 1.1 |  | Heat uncertainty factor is margin for underestimating heat loads
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1 |  | Fu is set to 1.00, however, using 35 MV/m is equivalent to Fu = 1.13
Heat load per cryogenic unit including uncertainty | (kW) | 33.5156 | 3.3728 | 2.6214
Mass flow per cryogenic unit including uncertainty | (g/s) | 160.6076 | 105.2352 | 126.8999
Weighted ideal power | (kW) | 154.3388 | 160.2259 | 405.4126
4.5 K equiv weighted power | (kW) | 2.3506 | 2.4402 | 6.1744 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 501.1001 | 606.9162 | 1675.2585 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 551.2101 | 667.6078 | 1842.7844 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 16.4464 | 197.9394 | 702.9849
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 |  | Overall multiplier = | 1.54 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 46.9218 | 4.7219 | 3.6699
Installed power | (kW) | 771.6941 | 934.6509 | 2579.8982
Installed 4.5 K equiv | (kW) | 3.5259 | 4.2704 | 11.7875
Installed 4.5 K equiv per unit length | (W/m) | 1.4262 | 1.7273 | 4.7679
Percent of total power at each level |  | 18% | 21.81% | 60.19%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 3.3399 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 3.6739 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 4.2862
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 19.5838
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.78335

## RDR revised
Tom Peterson |  |  | ILC Cryogenic Power Estimates
Includes updates to static and input coupler heat
This version: | ILC at 31.5 MV/m, 1.0x10^10, 5 Hz
1 standard cryogenic unit of 250 GeV linac.
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
2.4723
Total heat load (dynamic plus static) for 9-8-9 RF units, full cryogenic unit
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-8-8-8-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 192 | modules in this cryogenic unit (longest anticipated)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 75.0444 | 10.8172 | 1.3239 |  | Heat loads per CM_HeatLoad sheet
Predicted module dynamic heat load | (W/module) | 82.9489 | 7.049 | 10.0436
Number of modules per cryo unit (9-8-9-cavity modules) |  | 192 | 192 | 192
Total module static heat per cryo unit | (kW) | 14.4085 | 2.0769 | 0.25419
Total module dynamic heat per cryo unit | (kW) | 15.9262 | 1.3534 | 1.9284
Non-module heat load per cryo unit | (kW) | 1 | 0.2 | 0.2 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 31.3347 | 3.6303 | 2.3826 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 150.1568 | 113.2703 | 115.3387 |  |  | times 20 boxes per cryo unit
Ideal power based on total estimated heat | (kW) | 144.296 | 172.4598 | 368.4773
Heat uncertainty factor on static heat (Fus) |  | 1.1 | 1.1 | 1.1 |  | Heat uncertainty factor is margin for underestimating heat loads
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1 |  | Fu is set to 1.00, however, using 35 MV/m is equivalent to Fu = 1.13
Heat load per cryogenic unit including uncertainty | (kW) | 34.4682 | 3.9933 | 2.6208
Mass flow per cryogenic unit including uncertainty | (g/s) | 165.1725 | 124.5974 | 126.8725
Weighted ideal power | (kW) | 158.7256 | 189.7057 | 405.3251
4.5 K equiv weighted power | (kW) | 2.4174 | 2.8892 | 6.1731 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 515.3428 | 718.5823 | 1674.897 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 566.8771 | 790.4406 | 1842.3867 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 16.4464 | 197.9394 | 702.9849
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 |  | Overall multiplier = | 1.54 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 48.2555 | 5.5907 | 3.6691
Installed power | (kW) | 793.6279 | 1106.6168 | 2579.3414
Installed 4.5 K equiv | (kW) | 3.6261 | 5.0561 | 11.785
Installed 4.5 K equiv per unit length | (W/m) | 1.4667 | 2.0451 | 4.7669
Percent of total power at each level |  | 17.72% | 24.7% | 57.58%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 3.4906 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 3.8396 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 4.4796
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 20.4672
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.81869

## TDR Power KCS
Tom Peterson |  |  | ILC Cryogenic Power Estimates
2012-06-26
This sheet: | TDR Power KCS
1 standard cryogenic unit for the KCS arrangement into cryo strings and units
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
2.0087
Total heat load (dynamic plus static) for 9-8-9 RF units, full cryogenic unit
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-9-8-9-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 156 | modules in this cryogenic unit (longest anticipated)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383 |  |  | number of modules from cryogenics_parameters_KCS.xlsx
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 75.0444 | 10.8172 | 1.3239
Predicted module dynamic heat load | (W/module) | 58.7969 | 5.0475 | 9.7852 |  | Heat loads per CM_HeatLoad sheet
Number of modules per cryo unit (9-8-9-cavity modules) |  | 156 | 156 | 156
Total module static heat per cryo unit | (kW) | 11.7069 | 1.6875 | 0.20653
Total module dynamic heat per cryo unit | (kW) | 9.1723 | 0.78742 | 1.5265
Non-module heat load per cryo unit | (kW) | 0.7 | 0.14 | 0.14 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 21.5793 | 2.6149 | 1.873 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 103.4084 | 81.5882 | 90.6725 |  |  | times 14 boxes per cryo unit
Ideal power based on total estimated heat | (kW) | 99.3722 | 124.2222 | 289.6753
Heat uncertainty factor on static heat (Fus) |  | 1.1 | 1.1 | 1.1 |  | Heat uncertainty factor is margin for underestimating heat loads
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1
Heat load per cryogenic unit including uncertainty | (kW) | 23.7372 | 2.8764 | 2.0603
Mass flow per cryogenic unit including uncertainty | (g/s) | 113.7492 | 89.7471 | 99.7397
Weighted ideal power | (kW) | 109.3094 | 136.6444 | 318.6429
4.5 K equiv weighted power | (kW) | 1.6648 | 2.0811 | 4.8529 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 354.9007 | 517.5924 | 1316.706 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 390.3907 | 569.3516 | 1448.3766 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 16.4464 | 197.9394 | 702.9849
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 |  | Overall multiplier = | 1.54 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 33.2321 | 4.027 | 2.8845 |  | Vapor density (g/cc) | 0.0007936 |  | peak vapor velocity (cm/sec) | 249.0477
Installed power | (kW) | 546.547 | 797.0922 | 2027.7273 |  |  |  | including uncertainty and overcapacity factors
Installed 4.5 K equiv | (kW) | 2.4972 | 3.6419 | 9.2647 |  |  | 2 K mass flow with all factors | 139.6356
Installed 4.5 K equiv per unit length | (W/m) | 1.2432 | 1.8131 | 4.6123
Percent of total power at each level |  | 16.21% | 23.64% | 60.15%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 2.627 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 2.8897 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 3.3714 |  | 21.6113 | kW per module
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 15.4037
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.61615

## TDR Power DKS
Tom Peterson |  |  | ILC Cryogenic Power Estimates
2012-06-26
This sheet: | TDR Power DKS
1 standard cryogenic unit with DKS arrangement into cryo strings and cryo units
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
2.4336
Total heat load (dynamic plus static) for 9-8-9 RF units, full cryogenic unit
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-9-8-9-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 189 | modules in this cryogenic unit (longest anticipated)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383 |  |  | number of modules from cryogenics_parameters_DKS.xlsx
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 75.0444 | 10.8172 | 1.3239
Predicted module dynamic heat load | (W/module) | 58.7969 | 5.0475 | 9.7852 |  | Heat loads per CM_HeatLoad sheet
Number of modules per cryo unit (9-8-9-cavity modules) |  | 189 | 189 | 189
Total module static heat per cryo unit | (kW) | 14.1834 | 2.0445 | 0.25022
Total module dynamic heat per cryo unit | (kW) | 11.1126 | 0.95399 | 1.8494
Non-module heat load per cryo unit | (kW) | 1.1 | 0.22 | 0.22 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 26.396 | 3.2184 | 2.3196 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 126.4904 | 100.4193 | 112.2923 |  |  | times 22 boxes per cryo unit
Ideal power based on total estimated heat | (kW) | 121.5533 | 152.8935 | 358.7451
Heat uncertainty factor on static heat (Fus) |  | 1.1 | 1.1 | 1.1 |  | Heat uncertainty factor is margin for underestimating heat loads
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1
Heat load per cryogenic unit including uncertainty | (kW) | 29.0356 | 3.5403 | 2.5516
Mass flow per cryogenic unit including uncertainty | (g/s) | 139.1395 | 110.4613 | 123.5216
Weighted ideal power | (kW) | 133.7087 | 168.1828 | 394.6196
4.5 K equiv weighted power | (kW) | 2.0364 | 2.5614 | 6.01 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 434.119 | 637.0562 | 1630.6596 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 477.5309 | 700.7618 | 1793.7256 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 16.4464 | 197.9394 | 702.9849
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 |  | Overall multiplier = | 1.54 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 40.6499 | 4.9564 | 3.5722 |  | Vapor density (g/cc) | 0.0007936 |  | peak vapor velocity (cm/sec) | 308.4303
Installed power | (kW) | 668.5433 | 981.0665 | 2511.2158 |  |  |  | including uncertainty and overcapacity factors
Installed 4.5 K equiv | (kW) | 3.0546 | 4.4825 | 11.4737 |  |  | 2 K mass flow with all factors | 172.9302
Installed 4.5 K equiv per unit length | (W/m) | 1.2552 | 1.8419 | 4.7147
Percent of total power at each level |  | 16.07% | 23.58% | 60.35%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 3.2422 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 3.5664 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 4.1608 |  | 22.015 | kW per module
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 19.0108
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.76043

## e+ 5 GeV source
Tom Peterson |  |  | ILC Cryogenic Power Estimates
2012-06-26
This sheet: | 5 Hz LP KCS e+ (e+ source baseline) for e+ 5 GeV booster
1 standard cryogenic unit
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
0.33478
Total heat load (dynamic plus static) for 9-8-9 RF units, full cryogenic unit
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-9-8-9-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 26 | modules in this cryogenic unit (longest anticipated)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383 |  |  | number of modules from " ILC cryo RF layout labels.xlsx "
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 91.8033 | 12.8867 | 2.7267
Predicted module dynamic heat load | (W/module) | 77.4577 | 7.3181 | 6.5661 |  | Heat loads per CM_HeatLoad sheet
Number of modules per cryo unit (8-cavity modules) |  | 26 | 26 | 26
Total module static heat per cryo unit | (kW) | 2.3869 | 0.33505 | 0.070893
Total module dynamic heat per cryo unit | (kW) | 2.0139 | 0.19027 | 0.17072
Transfer line total length | (m) | 50 | 50 | 50 |  | Add 10 W, 10 W, and 50 W load total for other heat
Transfer line heat load per meter | (W) | 3.5309 | 0.49564 | 0.10487 |  | Assume large T-line equiv to empty CM, so static CM heat
Transfer line heat load total | (kW) | 0.17654 | 0.024782 | 0.0052436
End box heat load total | (kW) | 0.15 | 0.03 | 0.03 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 4.7273 | 0.58011 | 0.27685 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 22.6535 | 18.1001 | 13.4024 |  |  | times 3 boxes for e- source assuming 2 strings, 12 CM each
Ideal power based on total estimated heat | (kW) | 21.7693 | 27.5582 | 42.8174
Heat uncertainty factor on static heat (Fus) |  | 1.3 | 1.3 | 1.3 |  | Heat uncertainty factor is margin for underestimating heat loads, 1.3 for static due to boxes and T-lines
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1
Heat load per cryogenic unit including uncertainty | (kW) | 5.7428 | 0.71608 | 0.32577
Mass flow per cryogenic unit including uncertainty | (g/s) | 27.5194 | 22.3427 | 15.7703
Weighted ideal power | (kW) | 26.4453 | 34.0179 | 50.3821
4.5 K equiv weighted power | (kW) | 0.40276 | 0.51809 | 0.76732 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 77.7475 | 114.826 | 194.6244 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 94.4475 | 141.7413 | 229.0094 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 26.4453 | 34.0179 | 50.3821
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.7007 | 1.7282 | 1.6473 |  | Overall multiplier = | 1.682 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 8.0399 | 1.0025 | 0.45607 |  | Vapor density (g/cc) | 0.0007936 |  | peak vapor velocity (cm/sec) | 3.2461
Installed power | (kW) | 132.2265 | 198.4378 | 320.6132 |  |  |  | including uncertainty and overcapacity factors
Installed 4.5 K equiv | (kW) | 0.60414 | 0.90666 | 1.4649 |  |  | 2 K mass flow with all factors | 22.0784
Installed 4.5 K equiv per unit length | (W/m) | 1.8046 | 2.7082 | 4.3756
Percent of total power at each level |  | 20.3% | 30.47% | 49.23%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 0.46464 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 0.55824 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 0.65128 |  | 25.0491 | kW per module
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 2.9757
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.11903

## e- 5 GeV source
Tom Peterson |  |  | ILC Cryogenic Power Estimates
2012-06-26
This sheet: | 10 Hz LP KCS e- (e- source baseline) for e- 5 GeV booster plus positron production beam
1 standard cryogenic unit
Heat loads per attached CM_HeatLoad sheet (sheet 1)
| Module length based on Module-9-8-9-21Nov06.xls |  |  |  |  | approximate cryogenic unit length (km)
0.30903
Total heat load (dynamic plus static) for 9-8-9 RF units, e- source
|  | 40 K to 80 K | 5 K to 8 K | 2 K |  | Assumptions:
|  | Temperature level | Temperature level | Temperature level |  | Module length based on Module-9-8-9-21Nov06.xls
|  | (module) | (module) | (module) |  | 12668 | mm slot length for module with magnets and BPM
Temp in | (K) | 40 | 5 | 2.4 |  | 12668 | mm slot length for module without magnets and BPM
Press in | (bar) | 16 | 5 | 1.2 |  | 24 | modules in this cryogenic unit (e- source)
Enthalpy in | (J/g) | 223.78 | 14.66 | 4.383 |  |  | number of modules from " ILC cryo RF layout labels.xlsx "
Entropy in | (J/gK) | 15.3399 | 3.901 | 1.862
Temp out | (K) | 80 | 8 | 2 |  | Note: cells highlighted in yellow are independent variables, parameters that are entered
Press out | (bar) | 14 | 4 | saturated vapor
Enthalpy out | (J/g) | 432.46 | 46.71 | 25.04
Entropy out | (J/gK) | 19.2388 | 9.083 | 12.58
|  | 40 K to 80 K | 5 K to 8 K | 2 K
Predicted module static heat load | (W/module) | 75.3113 | 11.0247 | 1.5962
Predicted module dynamic heat load | (W/module) | 120.4383 | 10.803 | 10.5988 |  | Heat loads per CM_HeatLoad sheet
Number of modules per cryo unit (8-cavity modules) |  | 24 | 24 | 24
Total module static heat per cryo unit | (kW) | 1.8075 | 0.26459 | 0.038308
Total module dynamic heat per cryo unit | (kW) | 2.8905 | 0.25927 | 0.25437
Transfer line total length | (m) | 50 | 50 | 50
Transfer line heat load per meter | (W) | 3.138 | 0.45936 | 0.066507 |  | Assume large T-line equiv to empty CM, so static CM heat
Transfer line heat load total | (kW) | 0.1569 | 0.022968 | 0.0033253
End box heat load total | (kW) | 0.15 | 0.03 | 0.03 |  | Add 10 W, 10 W, and 50 W load total for other heat
Total predicted heat per cryogenic unit | (kW) | 5.0049 | 0.57683 | 0.326 |  |  | per cryo box at 2 K, 5 K and 40 K, respectively
Total predicted mass flow per cryo unit | (g/s) | 23.9836 | 17.9979 | 15.7818 |  |  | times 3 boxes for e- source assuming 2 strings, 12 CM each
Ideal power based on total estimated heat | (kW) | 23.0475 | 27.4027 | 50.4187
Heat uncertainty factor on static heat (Fus) |  | 1.3 | 1.3 | 1.3 |  | Heat uncertainty factor is margin for underestimating heat loads, 1.3 for static due to boxes and T-lines
Heat uncertainty factor on dynamic heat (Fud) |  | 1.1 | 1.1 | 1.1
Heat load per cryogenic unit including uncertainty | (kW) | 5.9283 | 0.69803 | 0.37293
Mass flow per cryogenic unit including uncertainty | (g/s) | 28.4083 | 21.7793 | 18.0535
Weighted ideal power | (kW) | 27.2995 | 33.1601 | 57.6763
4.5 K equiv weighted power | (kW) | 0.41577 | 0.50503 | 0.87841 |  |  | Cryoplant coefficient of performance (W/W)
Efficiency (fraction Carnot) |  | 0.28 | 0.24 | 0.22 |  |  | 40 K - 80 K | 5 K - 8 K | 2 K
Efficiency in Watts/Watt | (W/W) | 16.4464 | 197.9394 | 702.9849 |  | TESLA TDR: | 17 | 168 | 588
Operating power based on predicted heat | (kW) | 82.3123 | 114.1778 | 229.1761 |  | XFEL: | 20 | 220 | 870
Operating power including uncertainty | (kW) | 97.4983 | 138.1671 | 262.1651 |  | Industrial est: | 16.5 | 200 | 700 | adjusted eff to match these
[6 empty] | ILC assumption: | 16.4464 | 197.9394 | 702.9849
Overcapacity factor (Fo) |  | 1.4 | 1.4 | 1.4 |  | Overcapacity factor is margin for off-optimal operation and control
Overall net cryogenic capacity multiplier |  | 1.6583 | 1.6941 | 1.6015 |  | Overall multiplier = | 1.6373 | TESLA TDR: | 1.5
Heat load per cryogenic unit including Fus, Fud, and Fo | (kW) | 8.2996 | 0.97724 | 0.5221 |  | Vapor density (g/cc) | 0.0007936 |  | peak vapor velocity (cm/sec) | 45.0792
Installed power | (kW) | 136.4976 | 193.4339 | 367.0311 |  |  |  | including uncertainty and overcapacity factors
Installed 4.5 K equiv | (kW) | 0.62366 | 0.8838 | 1.677 |  |  | 2 K mass flow with all factors | 25.2749
Installed 4.5 K equiv per unit length | (W/m) | 2.0181 | 2.8599 | 5.4265
Percent of total power at each level |  | 19.58% | 27.75% | 52.66%
Total operating power for one cryo unit based on predicted heat (MW) |  |  | 0.5108 |  | Operating power includes 1.2 overcapacity factor for control only
Total operating power for one cryo unit including uncertainty factor (MW) |  |  | 0.5974 |  | Operating power includes 1.2 overcapacity factor for control only
Total installed power for one cryo unit (MW) |  |  | 0.69696 |  | 29.0401 | kW per module
Total installed 4.5 K equivalent power for one cryo unit (kW) |  |  | 3.1844
Fraction of largest practical cryoplant per cryogenic unit |  |  | 0.12738

## summary
Tom Peterson |  |  |  |  | RDR ML plant
2012-06-26 |  |  |  |  | installed power |  | total number | total installed
| 2 K total heat | 5 K total heat | 40 K total heat | Installed power | for reference | power ratio | of cryogenic plants | plant power
|  | (Watts per cryomodule, not including other heat) |  | (MW per cryoplant) | (MW per cryoplant) | new/RDR | of this size | (MW)
for reference: RDR | 11.3701 | 14.928 | 153.4829 | 4.2862 | 4.2862 | 1 | 10 | 42.8624
for reference: RDR revised | 11.3675 | 17.8662 | 157.9934 | 4.4796 | 4.2862 | 1.0451 | 10 | 44.7959
TDR KCS for ML + RTML | 11.1091 | 15.8648 | 133.8414 | 3.3714 | 4.2862 | 0.78656 | 12 | 40.4564
TDR DKS for ML + RTML | 11.1091 | 15.8648 | 133.8414 | 4.1608 | 4.2862 | 0.97074 | 10 | 41.6083
e+ 5 GeV source | 9.2927 | 20.2048 | 169.2611 | 0.65128 | 4.2862 | 0.15195 | 1 | 0.65128
e- 5 GeV source | 12.195 | 21.8277 | 195.7497 | 0.69696 | 4.2862 | 0.1626 | 1 | 0.69696